## COVER
LAPORAN TEKNIK PEMELIHARAAN RUTIN
SISTEM PROTEKSI BAY PENGHANTAR
PT PLN (PERSERO) UNIT INDUK TRANSMISI
JAWA BAGIAN TENGAH
|  |  |  | UPT | : | BEKASI
|  |  |  | ULTG | : | BEKASI
|  |  |  | GI / GITET | : | CIKARANG
|  |  |  | BAY | : | RAJAPAKSI #2
|  |  |  | TANGGAL | : | 11 JUNI 2026
| Spesifikasi Relai Proteksi Utama | [7 empty] | Spesifikasi Relai Proteksi Backup
| Merk Relai |  | : | ALSTOM |  |  |  |  | Merk Relai | : | SIEMENS
| Tipe Relai |  | : | P545916L7M0570K |  |  |  |  | Tipe Relai | : | 7SJ62
| No Serie |  | : | 33339701/06/15 |  |  |  |  | No Serie | : | BF-NR0403052052
| Tahun Operasi |  | : | [5 empty] | Tahun Operasi | : | -
| Rasio CT |  | : | 2000/1 |  |  |  |  | Rasio CT | : | 2000/1
| Rasio PT |  | : | 150000/100 |  |  |  |  | Alat Uji | : | OMICRON CMC-356
| Alat Uji |  | : | OMICRON CMC-356
KESIMPULAN HASIL PEMELIHARAAN RUTIN SISTEM PROTEKSI
|  |  | Hasil Assessment Proteksi |  |  |  | 1
Pelaksana | [7 empty] | Supervisi
1 | RIZKY WIRA HANDALAN
2 | RIKI H
3
4
5 | [7 empty] | ( ERVAN JAGI M W )
PT PLN (Persero) Unit Induk Transmisi Jawa Bagian Tengah
Sub Bidang Pemeliharaan Proteksi & meter
Tahun 2024

## LCD
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT |  | : | BEKASI
|  | ULTG |  | : | BEKASI
1.1 |  | Pengujian Arus Minimum Pickup LCD
|  | NO | Fasa | Setting Arus (Ampere) |  |  | Hasil Uji Pickup Arus (Ampere) |  | Nilai Error (Persen) |  |  | Assessment |  |  | Indikasi
|  | 1 | R-N | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP, PH A
|  | 2 | S-N | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP, PH B
|  | 3 | T-N | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP,PH C
|  | 4 | R-S | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP, PH A-B
|  | 5 | S-T | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP, PH B-C
|  | 6 | T-R | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP, PH C-A
|  | 7 | R-S-T | 0,2 |  |  | 0.24 |  | 20% |  |  | 6 |  | -1 | DIFF TRIP, PH A-B-C
|  | Assessment Pengujian Arus Minimum Pickup | [7 empty] | 6
1.2 |  | Pengujian Waktu Kerja Relai LCD
|  | NO | Fasa | Setting Waktu (s) |  |  |  | Hasil Pengujian Waktu Kerja (s) |  |  | Nilai Error (Persen) |  |  | Assessment
|  | 1 | R-N | 0 |  |  |  | 0.039 |  |  | 3.9% |  |  | 9 | #DIV/0!
|  | 2 | S-N | 0 |  |  |  | 0.038 |  |  | 3.8% |  |  | 9 | #DIV/0!
|  | 3 | T-N | 0 |  |  |  | 0.043 |  |  | 4.3% |  |  | 9 | #DIV/0!
|  | 4 | R-S | 0 |  |  |  | 0.036 |  |  | 3.6% |  |  | 9 | #DIV/0!
|  | 5 | S-T | 0 |  |  |  | 0.036 |  |  | 3.6% |  |  | 9 | #DIV/0!
|  | 6 | T-R | 0 |  |  |  | 0.037 |  |  | 3.7% |  |  | 9 | #DIV/0!
|  | 7 | R-S-T | 0 |  |  |  | 0.036 |  |  | 3.6% |  |  | 9 | #DIV/0!
|  | Assessment Pengujian Waktu Kerja Relai | [7 empty] | 9
1.3 |  | Pengujian Stability Sekunder LCD
|  | NO | Item Pengujian |  |  | Arus Lokal GI / GITET . |  |  | Arus Remote GI / GITET . |  |  |  | Hasil Pengujian (Trip/No Trip) |  |  | Pembacaan Nilai Diff & Rest
|  | 1 | Pengujian Beban Normal |  |  | R : 220 |  |  | R : | [6 empty] | Idiff : 0% & Irest : 25% .
[6 empty] | S : 227 |  |  | S : | [6 empty] | Idiff : 0% & Irest : 26% .
[6 empty] | T : 226 |  |  | T : | [6 empty] | Idiff : 0% & Irest : 25% .
|  | 2 | Pengujian Gangguan Eksternal 1 Fasa |  |  | R : |  |  | R : | [6 empty] | Idiff : & Irest : .
[6 empty] | S : |  |  | S : | [6 empty] | Idiff : & Irest : .
[6 empty] | T : |  |  | T : | [6 empty] | Idiff : & Irest : .
|  | 3 | Pengujian Gangguan Internal 1 Fasa |  |  | R : |  |  | R : | [6 empty] | Idiff : & Irest : .
[6 empty] | S : |  |  | S : | [6 empty] | Idiff : & Irest : .
[6 empty] | T : |  |  | T : | [6 empty] | Idiff : & Irest : .
*) Kosongkan jika tidak dilakukan pengujian
|  | Assessment Pengujian Stability Sekunder | [7 empty] | 9
1.4 |  | Evaluasi dan Keterangan
- Setting Idiff = 0,2 A - Pengujian Idiff PICK UP kondisi comm OK (tanpa loopback ) - Pengujian Waktu Kerja dengan injeksi 2x Idiff
1.5 |  | Kesimpulan :
|  | Assessment Pengujian Individu LCD | [7 empty] | 6
Pelaksana | [9 empty] | Supervisi
1 | RIZKY WIRA HANDALAN
2 | RIKI H
3
4
5 | [9 empty] | ( ERVAN JAGI M W )

## DISTANCE
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
2.1 |  | Pengujian Impedance Distance pada Sudut Line
|  | Jenis Gangguan |  |  | Parameter |  |  | R-N |  |  | S-N |  |  | T-N |  |  | R-S |  |  | S-T |  |  | T-R |  | R-S-T
|  | Z1 |  |  | Z Setting (Ω) |  |  | 0.4754 |  |  | 0.4754 |  |  | 0.4754 |  |  | 0.28 |  |  | 0.28 |  |  | 0.28 |  | 0.28
[5 empty] | Z Hasil (Ω) |  |  | 0.475 |  |  | 0.475 |  |  | 0.475 |  |  | 0.28 |  |  | 0.28 |  |  | 0.28 |  | 0.28
[5 empty] | % Error |  |  | -0.08414% |  |  | -0.08414% |  |  | -0.08414% |  |  | 0% |  |  | 0% |  |  | 0% |  | 0% |  | 0
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  | 9 |  | 0
|  | Z2 |  |  | Z Setting (Ω) |  |  | 1.8 |  |  | 1.8 |  |  | 1.8 |  |  | 1.06 |  |  | 1.06 |  |  | 1.06 |  | 1.06
[5 empty] | Z Hasil (Ω) |  |  | 1.823 |  |  | 1.823 |  |  | 1.823 |  |  | 1.073 |  |  | 1.047 |  |  | 1.073 |  | 1.073
[5 empty] | % Error |  |  | 1.278% |  |  | 1.278% |  |  | 1.278% |  |  | 1.226% |  |  | -1.226% |  |  | 1.226% |  | 1.226% |  | 0
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  | 9 |  | 0
|  | Z3 |  |  | Z Setting (Ω) |  |  | 4.16 |  |  | 4.16 |  |  | 4.16 |  |  | 2.45 |  |  | 2.45 |  |  | 2.45 |  | 2.45
[5 empty] | Z Hasil (Ω) |  |  | 4.2 |  |  | 4.2 |  |  | 4.2 |  |  | 2.465 |  |  | 2.465 |  |  | 2.465 |  | 2.496
[5 empty] | % Error |  |  | 0.9615% |  |  | 0.9615% |  |  | 0.9615% |  |  | 0.6122% |  |  | 0.6122% |  |  | 0.6122% |  | 1.878% |  | 0
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  | 9 |  | 0
|  | Assessment Pengujian Impedansi Distance | [9 empty] | 9
2.2 |  | Pengujian Waktu Kerja Distance pada Sudut Line
|  | Jenis Gangguan |  |  | Parameter |  |  | R-N |  |  | S-N |  |  | T-N |  |  | R-S |  |  | S-T |  |  | T-R |  | R-S-T
|  | Z1 |  |  | Setting (s) |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0
[5 empty] | Hasil (s) |  |  | 0.046 |  |  | 0.049 |  |  | 0.047 |  |  | 0.0478 |  |  | 0.0546 |  |  | 0.0546 |  | 0.0511
[5 empty] | % Error |  |  | 4.6% |  |  | 4.9% |  |  | 4.7% |  |  | 4.78% |  |  | 5.46% |  |  | 5.46% |  | 5.11% |  | 3
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 6 |  |  | 6 |  | 6 |  | 0
|  | Z2 |  |  | Setting (s) |  |  | 0.4 |  |  | 0.4 |  |  | 0.4 |  |  | 0.4 |  |  | 0.4 |  |  | 0.4 |  | 0.4
[5 empty] | Hasil (s) |  |  | 0.435 |  |  | 0.444 |  |  | 0.442 |  |  | 0.447 |  |  | 0.451 |  |  | 0.445 |  | 0.448
[5 empty] | % Error |  |  | 3.5% |  |  | 4.4% |  |  | 4.2% |  |  | 4.7% |  |  | 5.1% |  |  | 4.5% |  | 4.8% |  | 1
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 6 |  |  | 9 |  | 9 |  | 0
|  | Z3 |  |  | Setting (s) |  |  | 1.6 |  |  | 1.6 |  |  | 1.6 |  |  | 1.6 |  |  | 1.6 |  |  | 1.6 |  | 1.6
[5 empty] | Hasil (s) |  |  | 1.643 |  |  | 1.645 |  |  | 1.635 |  |  | 1.639 |  |  | 1.635 |  |  | 1.635 |  | 1.648
[5 empty] | % Error |  |  | 2.687% |  |  | 2.812% |  |  | 2.187% |  |  | 2.437% |  |  | 2.187% |  |  | 2.187% |  | 3% |  | 0
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  | 9 |  | 0
|  | Assessment Pengujian Waktu Kerja Distance | [9 empty] | 6
2.3 |  | Pengujian Impedance Distance pada Sudut 0° dan 90°
|  | Jenis Gangguan |  |  | Parameter |  |  | Sudut 0° atau Nilai X | [8 empty] | Sudut 90° atau Nilai R
[8 empty] | R-N |  |  | S-N |  |  | T-N |  |  | R-N |  |  | S-N |  |  | T-N
|  | Z1 |  |  | Z Setting (Ω) |  |  | 9.061 |  |  | 9.061 |  |  | 9.061 |  |  | 0.474 |  |  | 0.474 |  |  | 0.474
[5 empty] | Z Hasil (Ω) |  |  | 7.017 |  |  | 7.017 |  |  | 7.491 |  |  | 0.474 |  |  | 0.474 |  |  | 0.474
[5 empty] | % Error |  |  | -22.56% |  |  | -22.56% |  |  | -17.33% |  |  | 0% |  |  | 0% |  |  | 0% |  | 1
[5 empty] | Assessment |  |  | 1 |  |  | 1 |  |  | 6 |  |  | 9 |  |  | 9 |  |  | 9 |  | 2
|  | Z2 |  |  | Z Setting (Ω) |  |  | 29.21 |  |  | 29.21 |  |  | 29.21 |  |  | 1.798 |  |  | 1.798 |  |  | 1.798
[5 empty] | Z Hasil (Ω) |  |  | 29.21 |  |  | 29.21 |  |  | 29.21 |  |  | 1.821 |  |  | 1.821 |  |  | 1.821
[5 empty] | % Error |  |  | 0% |  |  | 0% |  |  | 0% |  |  | 1.279% |  |  | 1.279% |  |  | 1.279% |  | 0
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  | 0
|  | Z3 |  |  | Z Setting (Ω) |  |  | 32.46 |  |  | 32.46 |  |  | 32.46 |  |  | 4.155 |  |  | 4.155 |  |  | 4.155
[5 empty] | Z Hasil (Ω) |  |  | 32.34 |  |  | 32.58 |  |  | 32.34 |  |  | 4.223 |  |  | 4.196 |  |  | 4.196
[5 empty] | % Error |  |  | -0.3697% |  |  | 0.3697% |  |  | -0.3697% |  |  | 1.637% |  |  | 0.9868% |  |  | 0.9868% |  | 0
[5 empty] | Assessment |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 |  | 0
|  | Assessment Pengujian Impedance Distance pada Sudut 0° dan 90° | [9 empty] | 1
2.4 |  | Pengujian Aided DEF Aided
|  | Jenis Gangguan |  | Arus Pickup (Ampere) | [8 empty] | Waktu Kerja (s) | [8 empty] | Assessment |  | Indikasi
|  |  |  | Setting |  |  | Hasil Uji |  |  | Error |  |  | Setting |  |  | Hasil Uji |  |  | Error
|  | R-N | [7 empty] | 0% | [8 empty] | 0% |  |  | 9
|  | S-N | [7 empty] | 0% | [8 empty] | 0% |  |  | 9
|  | T-N | [7 empty] | 0% | [8 empty] | 0% |  |  | 9
|  | Assessment Pengujian Aided DEF Main | [9 empty] | 9
2.5 |  | Pengujian Current Reversal
|  | Kondisi Fungsi Current Reversal |  |  |  | Pengujian | [5 empty] | Waktu Kerja (s) |  |  | Assessment |  |  | Indikasi
|  | Non Aktif |  |  |  | DEF Reverse --> DEF Forward + Receive | [8 empty] | 9
|  | Aktif | [12 empty] | 9
|  | Assessment Pengujian Current Reversal | [9 empty] | 9
2.6 |  | Pengujian DEF Backup
|  | Jenis Gangguan |  | Arus Pickup | [8 empty] | Waktu Kerja (s) | [8 empty] | Assessment |  | Indikasi
|  |  |  | Setting |  |  | Hasil Uji |  |  | Error |  |  | Setting |  |  | Hasil Uji |  |  | Error
|  | R-N | [7 empty] | 0% | [8 empty] | 0% |  |  | 9
|  | S-N | [7 empty] | 0% | [8 empty] | 0% |  |  | 9
|  | T-N | [7 empty] | 0% | [8 empty] | 0% |  |  | 9
|  | Assessment Pengujian DEF Backup | [9 empty] | 9
2.7 |  | Pengujian Fungsi SOTF/TOR
|  | Kondisi Fungsi SOTF |  |  |  | Pengujian | [5 empty] | Waktu Kerja (s) |  |  | Assessment |  |  | Indikasi
|  | SOTF OFF |  |  |  | Zone 2 (I = 1,2 x In) | [5 empty] | 0.439 |  |  | 9
|  | SOTF ON |  |  |  | Zone 2 (I = 1,2 x In) | [5 empty] | 0.021 |  |  | 9
|  | SOTF ON* |  |  |  | Zone Reverse (I = 1,2 x In) | [5 empty] | - |  |  | 9
*) Jika tidak trip, maka isi waktu kerja dengan " - "
|  | Assessment Pengujian Fungsi SOTF/TOR | [9 empty] | 9
2.8 |  | Pengujian VT Fail
|  | Jenis Tegangan Hilang |  |  | Fasa Tegangan Hilang |  |  |  | Hasil Pengujian | [5 empty] | Assessment |  |  | Indikasi
[9 empty] | Trip |  |  | Block
|  | 1 Fasa |  |  | R | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
[5 empty] | S | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
[5 empty] | T | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
|  | 2 Fasa |  |  | R-S | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
[5 empty] | S-T | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
[5 empty] | T-R | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
|  | 3 Fasa |  |  | RST | [6 empty] | v |  |  | 9 |  |  | VT FAIL ALARM
|  | Assessment Pengujian VT Fail | [9 empty] | 9
2.9 |  | Pengujian Pola Teleproteksi PUTT
|  | GI/GITET Lokal …..................................... | [12 empty] | GI/GITET Remote ….....................................
|  | Jenis Gangguan |  |  | Teleproteksi (Send/Recv) |  |  |  | Waktu Kerja (s) |  |  | Assessment |  |  | Jenis Gangguan |  |  |  | Teleproteksi (Send/Recv) |  |  |  | Waktu Kerja (s) |  | Assessment
|  | Zone 1 / R-N | [9 empty] | 9 |  |  | Zone 2 / R-N | [9 empty] | 9
|  | Zone 1 / S-N | [9 empty] | 9 |  |  | Zone 2 / S-N | [9 empty] | 9
|  | Zone 1 / T-N | [9 empty] | 9 |  |  | Zone 2 / T-N | [9 empty] | 9
|  | Zone 1 / R-S | [9 empty] | 9 |  |  | Zone 2 / R-S | [9 empty] | 9
|  | Zone 1 / S-T | [9 empty] | 9 |  |  | Zone 2 / S-T | [9 empty] | 9
|  | Zone 1 / T-R | [9 empty] | 9 |  |  | Zone 2 / T-R | [9 empty] | 9
|  | Zone 1 / RST | [9 empty] | 9 |  |  | Zone 2 / RST | [9 empty] | 9
|  | Zone 2 / R-N | [9 empty] | 9 |  |  | Zone 1 / R-N | [9 empty] | 9
|  | Zone 2 / S-N | [9 empty] | 9 |  |  | Zone 1 / S-N | [9 empty] | 9
|  | Zone 2 / T-N | [9 empty] | 9 |  |  | Zone 1 / T-N | [9 empty] | 9
|  | Zone 2 / R-S | [9 empty] | 9 |  |  | Zone 1 / R-S | [9 empty] | 9
|  | Zone 2 / S-T | [9 empty] | 9 |  |  | Zone 1 / S-T | [9 empty] | 9
|  | Zone 2 / T-R | [9 empty] | 9 |  |  | Zone 1 / T-R | [9 empty] | 9
|  | Zone 2 / RST | [9 empty] | 9 |  |  | Zone 1 / RST | [9 empty] | 9
|  | Reverse / R-N | [6 empty] | - |  |  | 9 |  |  | Zone 1 / R-N | [9 empty] | 9
|  | Zone 1 / S-T | [9 empty] | 9 |  |  | Reverse / S-T | [7 empty] | - |  | 9
*) Jika tidak trip, maka isi waktu kerja dengan " - "
[12 empty] | 0 | 0 | [11 empty] | 0 | 0
|  | Assessment Pengujian Teleproteksi PUTT | [9 empty] | 9
2.10 |  | Pengujian Pola Teleproteksi POTT
|  | GI/GITET Lokal …..................................... | [12 empty] | GI/GITET Remote ….....................................
|  | Jenis Gangguan |  |  | Teleproteksi (Send/Recv) |  |  |  | Waktu Kerja (s) |  |  | Assessment |  |  | Jenis Gangguan |  |  |  | Teleproteksi (Send/Recv) |  |  |  | Waktu Kerja (s) |  | Assessment
|  | Zone 2 / R-N | [9 empty] | 9 |  |  | Zone 2 / R-N | [9 empty] | 9
|  | Zone 2 / S-N | [9 empty] | 9 |  |  | Zone 2 / S-N | [9 empty] | 9
|  | Zone 2 / T-N | [9 empty] | 9 |  |  | Zone 2 / T-N | [9 empty] | 9
|  | Zone 2 / R-S | [9 empty] | 9 |  |  | Zone 2 / R-S | [9 empty] | 9
|  | Zone 2 / S-T | [9 empty] | 9 |  |  | Zone 2 / S-T | [9 empty] | 9
|  | Zone 2 / T-R | [9 empty] | 9 |  |  | Zone 2 / T-R | [9 empty] | 9
|  | Zone 2 / RST | [9 empty] | 9 |  |  | Zone 2 / RST | [9 empty] | 9
|  | Reverse / R-N | [6 empty] | - |  |  | 9 |  |  | Zone 2 / R-N | [9 empty] | 9
|  | Zone 2 / S-T | [9 empty] | 9 |  |  | Reverse / S-T | [7 empty] | - |  | 9
*) Jika tidak trip, maka isi waktu kerja dengan " - "
[12 empty] | 0 | 0 | [11 empty] | 0 | 0
|  | Assessment Pengujian Teleproteksi POTT | [9 empty] | 9
2.11 |  | Pengujian Power Swing Block (PSB)
|  | Kondisi Fungsi PSB |  |  |  | Hasil Pengujian (Trip / No Trip) |  |  |  | Assessment |  |  |  |  | Indikasi
|  | Non Aktif | [7 empty] | 9
|  | Aktif |  |  |  | No Trip |  |  |  | 9 |  |  |  |  | PSB BLOCKED
|  | Assessment Pengujian PSB | [9 empty] | 9
2.12 |  | Pengujian Fault Locator (FL) di Sudut Line
|  | Jenis Pengujian | [6 empty] | Panjang PHT (km) |  |  |  | 25% Z Line (km) |  |  |  | 50% Z Line (km) |  |  |  | 75% Z Line (km) |  |  | 100% Z Line (km)
|  | Fasa R-S |  |  | Nilai Estimasi | [7 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0
Hasil Uji
[5 empty] | Error (%) | [7 empty] | 0% |  |  |  | 0% |  |  |  | 0% |  |  | 0% |  |  | 0
[5 empty] | Assessment | [7 empty] | 9 |  |  |  | 9 |  |  |  | 9 |  |  | 9 |  |  | 0
|  | Fasa S-T |  |  | Nilai Estimasi | [7 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0
Hasil Uji
[5 empty] | Error (%) | [7 empty] | 0% |  |  |  | 0% |  |  |  | 0% |  |  | 0% |  |  | 0
[5 empty] | Assessment | [7 empty] | 9 |  |  |  | 9 |  |  |  | 9 |  |  | 9 |  |  | 0
|  | Fasa T-R |  |  | Nilai Estimasi | [7 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0
Hasil Uji
[5 empty] | Error (%) | [7 empty] | 0% |  |  |  | 0% |  |  |  | 0% |  |  | 0% |  |  | 0
[5 empty] | Assessment | [7 empty] | 9 |  |  |  | 9 |  |  |  | 9 |  |  | 9 |  |  | 0
|  | Assessment Pengujian FL | [9 empty] | 9
2.13 |  | Evaluasi dan Keterangan
Sudut 0 deg = nilai R Sudut 90 deg = nilai X
2.14 |  | Kesimpulan :
|  | Assessment Pengujian Individu Distance | [9 empty] | 1
Pelaksana | [13 empty] | Supervisi
1 | RIZKY WIRA HANDALAN
2 | RIKI H
3
4
5 | [13 empty] | ( ERVAN JAGI M W )

## OCR-GFR
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
3 |  | Setting OCR dan GFR yang Diterapkan
|  | Setting Arus Pickup OCR |  |  |  | : | 0,86 |  | A
|  | Setting TMS OCR |  |  |  | : | 0,38
|  | Setting Arus Pickup GFR |  |  |  | : | 0,14 |  | A
|  | Setting TMS GFR |  |  |  | : | 0,69
3.1 |  | Pengujian Pickup dan Dropoff OCR/GFR
|  | Jenis Pengujian |  |  | Parameter |  |  | OCR R |  |  | OCR S | OCR T | GFR
|  | Pickup |  |  | Hasil Uji (A) |  |  | 0,95 |  |  | 0,95 | 0,95 | 0,15
[5 empty] | % Error |  |  | 10.47% |  |  | 10.47% | 10.47% | 7.143% | 1
[5 empty] | Assessment |  |  | 1 |  |  | 1 | 1 | 6 | 3
|  | Dropoff |  |  | Hasil Uji (A) |  |  | 0,89 |  |  | 0,89 | 0,89 | 0,143
[5 empty] | % Rasio DO/PU |  |  | 93.68% |  |  | 93.68% | 93.68% | 95.33% | 3
[5 empty] | Assessment |  |  | 6 |  |  | 6 | 6 | 9 | 0
|  | Assessment Pengujian Pickup dan Dropoff | [7 empty] | 1
3.2 |  | Pengujian Karakteristik Waktu Kerja OCR/GFR
|  | Poin Pengujian |  |  | Parameter |  |  | 1.5 x Iset |  |  | 2.0 x Iset | 2.5 x Iset | 3.0 x Iset
|  | OCR Fasa R |  |  | Arus Injeksi (A) |  |  | 1.29 |  |  | 1.72 | 2.15 | 2.58
[5 empty] | Hasil Kalkulasi (s) |  |  | 6.5338 |  |  | 3.811 | 2.8765 | 2.3947
[5 empty] | Hasil Uji (s) |  |  | 6.543 |  |  | 3.816 |  | 2.393
[5 empty] | % Error |  |  | 0.1408% |  |  | 0.1304% | -100% | -0.0724%
|  | OCR Fasa S |  |  | Arus Injeksi (A) |  |  | 1.29 |  |  | 1.72 | 2.15 | 2.58 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  | 6.5338 |  |  | 3.811 | 2.8765 | 2.3947
[5 empty] | Hasil Uji (s) |  |  | 6.554 |  |  | 3.814 |  | 2.403
[5 empty] | % Error |  |  | 0.3091% |  |  | 0.07792% | -100% | 0.3452%
|  | OCR Fasa T |  |  | Arus Injeksi (A) |  |  | 1.29 |  |  | 1.72 | 2.15 | 2.58
[5 empty] | Hasil Kalkulasi (s) |  |  | 6.5338 |  |  | 3.811 | 2.8765 | 2.3947
[5 empty] | Hasil Uji (s) |  |  | 6.546 |  |  | 3.813 |  | 2.404
[5 empty] | % Error |  |  | 0.1867% |  |  | 0.05169% | -100% | 0.3869%
|  | GFR |  |  | Arus Injeksi (A) |  |  | 0.21 |  |  | 0.28 | 0.35 | 0.42 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  | 11.864 |  |  | 6.92 | 5.2231 | 4.3483
[5 empty] | Hasil Uji (s) |  |  | 11.87 |  |  | 6.934 |  | 4.356
[5 empty] | % Error |  |  | 0.05048% |  |  | 0.2019% | -100% | 0.1763%
|  | Kalkulasi Error Terbesar | [5 empty] | 0.3091% |  |  | 0.2019% | 100% | 0.3869%
|  | Hasil Asesmen | [5 empty] | 9 |  |  | 9 | 1 | 9
|  | Assessment Pengujian Karakteristik Waktu Kerja | [7 empty] | 1
3.3 |  | Evaluasi dan Keterangan
3.4 |  | Kesimpulan :
|  | Assessment Pengujian Individu OCR/GFR | [7 empty] | 1
Pelaksana | [10 empty] | Supervisi
1 | RIZKY WIRA H
2 | RIKI H
3
4
5 | [10 empty] | ( ERVAN JAGI M W )

## UJI FUNGSI
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
4.1 |  | Pengujian Fungsi LCD Terhadap Fungsi Distance & DEF Main
|  | Status LCD |  | Pengujian Distance / DEF Main |  | Kinerja Acuan |  |  | Hasil Uji |  |  | Assessment | Indikasi
|  | Com OK |  | Zone 1 |  | LCD Op |  |  | LCD Op |  |  | 9 | DIFF TRIP
|  | Com Fail |  | Zone 1 |  | Zone 1 Op |  |  | Zone 1 Op |  |  | 9 | Z1 TRIP
|  | Com OK |  | Zone 2 |  | LCD Op |  |  | LCD Op |  |  | 9 | DIFF TRIP
|  | Com Fail |  | Zone 2 |  | Zone 2 Op |  |  | Zone 2 Op |  |  | 9 | Z2 TRIP
|  | Com OK |  | Zone 3 |  | LCD Op |  |  | LCD Op |  |  | 9 | DIFF TRIP
|  | Com Fail |  | Zone 3 |  | Zone 3 Op |  |  | Zone 3 Op |  |  | 9 | Z3 TRIP
|  | Com OK |  | Zone 2 Aided |  | LCD Op |  |  | LCD Op |  |  | 9 | DIFF TRIP
|  | Com Fail |  | Zone 2 Aided |  | Zone 2 Aided Op | [5 empty] | 9
|  | Com OK |  | DEF Aided |  | LCD Op | [5 empty] | 9
|  | Com Fail |  | DEF Aided |  | DEF Aided Op | [5 empty] | 9
*) Seluruh pengujian menggunakan arus uji di atas setting I Diff
|  | Assessment Pengujian Fungsi LCD | [5 empty] | 9
4.2 |  | Pengujian Fungsi Main Proteksi
|  | Mode Autoreclose (SPAR / TPAR / STPAR) | [5 empty] | STPAR
|  | Fungsi Proteksi |  |  | Pengujian Fasa |  | Status AR |  | Kinerja Acuan |  |  | Hasil Uji | Assessment | Indikasi Relai, Annunciator & Lockout
|  | LCD |  |  | R |  | ON |  | Trip 1 Fasa R & Reclose |  |  |  | 9
|  | LCD |  |  | S |  | ON |  | Trip 1 Fasa S & Reclose |  |  |  | 9
|  | LCD |  |  | T |  | ON |  | Trip 1 Fasa T & Reclose |  |  |  | 9
|  | LCD |  |  | R |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA R, TRIP DIFF
|  | LCD |  |  | S |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA S, TRIP DIFF
|  | LCD |  |  | T |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA T, TRIP DIFF
|  | LCD |  |  | 2Ph |  | ON |  | Trip 3 Fasa & Reclose |  |  |  | 9
|  | LCD |  |  | 2Ph |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA TR, TRIP DIFF
|  | LCD |  |  | 3Ph |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | Zone 1 |  |  | R |  | ON |  | Trip 1 Fasa R & Reclose |  |  |  | 9
|  | Zone 1 |  |  | S |  | ON |  | Trip 1 Fasa S & Reclose |  |  |  | 9
|  | Zone 1 |  |  | T |  | ON |  | Trip 1 Fasa T & Reclose |  |  |  | 9
|  | Zone 1 |  |  | R |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA R, TRIP Z1
|  | Zone 1 |  |  | S |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA S, TRIP Z1
|  | Zone 1 |  |  | T |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA T, TRIP Z1
|  | Zone 1 |  |  | 2Ph |  | ON |  | Trip 3 Fasa & Reclose |  |  |  | 9
|  | Zone 1 |  |  | 2Ph |  | OFF |  | Trip 3 Fasa |  |  | Trip 3 Fasa | 9 | TRIP PHASA RT, TRIP Z1
|  | Zone 1 |  |  | 3Ph |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | Zone 2 |  |  | 1Ph |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | Zone Aided |  |  | R |  | ON |  | Trip 1 Fasa R & Reclose |  |  |  | 9
|  | Zone Aided |  |  | S |  | ON |  | Trip 1 Fasa S & Reclose |  |  |  | 9
|  | Zone Aided |  |  | T |  | ON |  | Trip 1 Fasa T & Reclose |  |  |  | 9
|  | Zone Aided |  |  | 1Ph |  | OFF |  | Trip 3 Fasa |  |  |  | 9
|  | Zone Aided |  |  | 2Ph |  | ON |  | Trip 3 Fasa & Reclose |  |  |  | 9
|  | Zone Aided |  |  | 2Ph |  | OFF |  | Trip 3 Fasa |  |  |  | 9
|  | Zone 3 |  |  | 1Ph |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | LCD/Zone 1 CB AB CLOSE CB Busbar OPEN |  |  | 1Ph |  | ON |  | Trip & Reclose CB AB CB Busbar Open |  |  |  | 9
|  | LCD/Zone 1 CB AB OPEN CB Busbar CLOSE |  |  | 1Ph |  | ON |  | Trip & Reclose CB Busbar CB AB Open |  |  |  | 9
|  | LCD/Zone 1 CB AB CLOSE CB Busbar CLOSE |  |  | 1Ph |  | ON |  | Trip & Reclose CB Busbar & AB |  |  |  | 9
|  | DEF BackUp |  |  | R |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | DEF BackUp |  |  | S |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | DEF BackUp |  |  | T |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | DEF Aided |  |  | R |  | ON |  | Trip 1 Fasa R & Reclose |  |  |  | 9
|  | DEF Aided |  |  | S |  | ON |  | Trip 1 Fasa S & Reclose |  |  |  | 9
|  | DEF Aided |  |  | T |  | ON |  | Trip 1 Fasa T & Reclose |  |  |  | 9
|  | DEF Aided |  |  | 1Ph |  | OFF |  | Trip 3 Fasa |  |  |  | 9
|  | Zone 1 |  |  | Ph R kemudian inject kembali Ph R pada masa RECLAIM time AR |  | ON |  | Trip 1 Fasa R & Disusul Trip Fasa ST |  |  |  | 9
|  | Zone 1 |  |  | Ph S kemudian inject kembali Ph T pada masa DEAD time AR |  | ON |  | Trip 1 Fasa S & Disusul Trip Fasa RT, Kemudian Reclose |  |  |  | 9
|  | PSB |  |  | Any Phase |  | ON |  | Tidak Trip |  |  |  | 9
|  | CURRENT REVERSAL |  |  | Zone 2 + Receive dengan waktu injek di bawah setting T Reversal |  | ON |  | Tidak Trip |  |  |  | 9
|  | CURRENT REVERSAL |  |  | DEF + Receive dengan waktu injek di atas setting T Reversal |  | ON |  | Tidak Trip |  |  |  | 9
|  | VT FAILURE |  |  | 1 Ph |  | ON |  | Tidak Trip |  |  | Tidak Trip | 9 | VT FAIL ALARM
|  | VT FAILURE |  |  | 3 Ph |  | ON |  | Tidak Trip |  |  | Tidak Trip | 9 | VT FAIL ALARM
|  | LCD/Z1 + CB not Healthy |  |  | 1Ph |  | ON |  | Trip 3 Fasa |  |  |  | 9
|  | Assessment Pengujian Fungsi Main Proteksi | [5 empty] | 9
4.3 |  | Pengujian Fungsi Backup Proteksi
|  | Fungsi Proteksi |  |  | Pengujian Fasa |  | Kinerja Acuan |  |  |  | Hasil Uji |  | Assessment | Indikasi Relai, Annunciator & Lockout
|  | OCR |  |  | RST |  | Trip 3 Fasa, Lockout |  |  |  | Trip 3 Fasa, Lockout |  | 9 | Rele Trip. OCR PU R-S-T
|  | GFR |  |  | N |  | Trip 3 Fasa, Lockout |  |  |  | Trip 3 Fasa, Lockout |  | 9 | Rele Trip, GF PU
|  | Assessment Pengujian Fungsi Backup Proteksi | [5 empty] | 9
4.4 |  | Evaluasi dan Keterangan
- AR normal off karena SKTT
4.5 |  | Kesimpulan :
|  | Assessment Pengujian Fungsi Keseluruhan | [5 empty] | 9
Pelaksana | [9 empty] | Supervisi
1 | RIZKY WIRA HANDALAN
2 | RIKI H
3
4
5 | [9 empty] | ( ERVAN JAGI M W )

## DATA VALIDASI (hidden)
LCD Op | SPAR | Trip 1 Fasa R & Reclose | Trip 3 Fasa, Lockout | Trip
Zone 1 Op | STPAR | Trip 1 Fasa S & Reclose | Trip 1 Fasa | No Trip
Zone 2 Op |  | Trip 1 Fasa T & Reclose | Tidak Trip
Zone 3 Op |  | Trip 3 Fasa
Zone 2 Aided Op |  | Trip 3 Fasa & Reclose
DEF Aided Op |  | Trip & Reclose CB AB CB Busbar Open
Trip & Reclose CB Busbar CB AB Open
Trip & Reclose CB Busbar & AB
Trip 1 Fasa R & Disusul Trip Fasa ST
Trip 1 Fasa S & Disusul Trip Fasa RT
Tidak Trip