## COVER
LAPORAN TEKNIK PEMELIHARAAN RUTIN
SISTEM PROTEKSI BAY IBT 500/150 KV
PT PLN (PERSERO) UNIT INDUK TRANSMISI
JAWA BAGIAN TENGAH
|  |  |  | UPT |  | : | BEKASI
|  |  |  | ULTG |  | : | BEKASI
|  |  |  | GI / GITET |  | : | GITET 500 KV MUARATAWAR
|  |  |  | BAY |  | : | IBT #1 500MVA
|  |  |  | TANGGAL |  | : | 2026-04-07
| Spesifikasi Relai Proteksi Diff Main A | [8 empty] | Spesifikasi Relai Proteksi Diff Main B
| Merk Relai |  | : | ALSTOM | [5 empty] | Merk Relai | : | GE MULTILIN
| Tipe Relai |  | : | MICOM P643 | [5 empty] | Tipe Relai | : | T60
| No Serie |  | : | 34196700/09/17 | [5 empty] | No Serie | : | ABHC17000986
| Tahun Operasi |  | : | 2025 | [5 empty] | Tahun Operasi | : | 2025
| Rasio CT HV |  | : | 1000/1 A | [5 empty] | Rasio CT HV | : | 1000/1 A
| Rasio CTN HV |  | : | 1000/1 A | [5 empty] | Rasio CTN HV | : | 1000/1 A
| Rasio CT LV |  | : | 2000/1 A | [5 empty] | Rasio CT LV | : | 2000/1 A
| Rasio CTN LV |  | : | 2500/1 A | [5 empty] | Rasio CTN LV | : | 2500/1 A
| Alat Uji |  | : | OMICRON 356 | [5 empty] | Alat Uji | : | OMICRON 356
| Spesifikasi Relai Proteksi CCP Main A | [8 empty] | Spesifikasi Relai Proteksi CCP Main B
| Merk Relai |  | : | ALSTOM | [5 empty] | Merk Relai | : | GE MULTILIN
| Tipe Relai |  | : | MICOM P643 | [5 empty] | Tipe Relai | : | T60
| No Serie |  | : | 34136689/09/17 | [5 empty] | No Serie | : | ABHC17000989
| Tahun Operasi |  | : | 2025 | [5 empty] | Tahun Operasi | : | 2025
| Rasio CT AB |  | : | 2000/1 A | [5 empty] | Rasio CT HV | : | 2000/1 A
| Rasio CT B |  | : | 2000/1 A | [5 empty] | Rasio CTN HV | : | 2000/1 A
| Rasio CT Line |  | : | 2000/1 A | [5 empty] | Rasio CT LV | : | 2000/1 A
| Alat Uji |  | : | OMICRON 356 | [5 empty] | Alat Uji | : | OMICRON CMC356
| Spesifikasi Relai Proteksi OCR/GFR 500 kV | [8 empty] | Spesifikasi Relai Proteksi OCR/GFR 150 kV
| Merk Relai |  | : | SCHNEIDER | [5 empty] | Merk Relai | : | SCHNEIDER
| Tipe Relai |  | : | P7 | [5 empty] | Tipe Relai | : | P5
| No Serie |  | : | SM2506564600002 | [5 empty] | No Serie | : | P5F30WSM24361600016
| Tahun Operasi |  | : | 2025 | [5 empty] | Tahun Operasi | : | 2025
| Rasio CT |  | : | 1000/1 A | [5 empty] | Rasio CT | : | 2000/1 A
| Alat Uji |  | : | OMICRON CMC356 | [5 empty] | Alat Uji | : | OMICRON CMC356
Spesifikasi Relai Proteksi NVDR
[5 empty] | Merk Relai |  |  | : | ALSTOM
[5 empty] | Tipe Relai |  |  | : | MICOM P143
[5 empty] | No Serie |  |  | : | 34193362/08/17
[5 empty] | Tahun Operasi |  |  | : | 2025
[5 empty] | Rasio VT |  |  | : | 66000/100 V
[5 empty] | Alat Uji |  |  | : | -
KESIMPULAN HASIL PEMELIHARAAN RUTIN SISTEM PROTEKSI
|  |  | Hasil Assessment Proteksi |  |  |  |  | 6
Pelaksana | [8 empty] | Supervisi
1 | RIZKY W. H.
2 | RIKI H.
3 | EDWAR D. V.
4
5 | [8 empty] | ERVAN JAGI M W
PT PLN (Persero) Unit Induk Transmisi Jawa Bagian Tengah
Sub Bidang Pemeliharaan Proteksi & meter
Tahun 2024

## DIFF-REF MAIN A
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT |  | : | BEKASI
|  | ULTG |  | : | BEKASI
1.1 |  | Pengujian Arus Minimum Pickup DIFF Sisi HV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0.173 | 0.172 | -0.578% |  |  |  | DIFF TRIP Ph R
|  | 2 |  | S *) |  | 0.173 | 0.172 | -0.578% |  |  |  | DIFF TRIP Ph S
|  | 3 |  | T *) |  | 0.173 | 0.172 | -0.578% |  |  |  | DIFF TRIP Ph T
|  | 4 |  | RST |  | 0.173 | 0.172 | -0.578% |  | 9 | -1 | DIFF TRIP Ph R-S-T
|  | Assessment Pengujian Arus Minimum Pickup HV | [6 empty] | 9
1.2 |  | Pengujian Waktu Kerja Diff Sisi HV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0 | 0.03 | 3% |  | 9 | #DIV/0! | DIFF TRIP Ph R
|  | 2 |  | S *) |  | 0 | 0.031 | 3.1% |  | 9 | #DIV/0! | DIFF TRIP Ph S
|  | 3 |  | T *) |  | 0 | 0.031 | 3.1% |  | 9 | #DIV/0! | DIFF TRIP Ph T
|  | 4 |  | RST |  | 0 | 0.032 | 3.2% |  | 9 | #DIV/0! | DIFF TRIP Ph R-S-T
|  | Assessment Pengujian Waktu Kerja Diff Sisi HV | [6 empty] | 9
1.3 |  | Pengujian Arus Minimum Pickup Sisi LV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0.289 | 0.285 | -1.384% |  |  |  | DIFF TRIP Ph R
|  | 2 |  | S *) |  | 0.289 | 0.285 | -1.384% |  |  |  | DIFF TRIP Ph S
|  | 3 |  | T *) |  | 0.289 | 0.285 | -1.384% |  |  |  | DIFF TRIP Ph T
|  | 4 |  | RST |  | 0.289 | 0.286 | -1.038% |  | 9 | -1 | DIFF TRIP Ph R-S-T
|  | Assessment Pengujian Arus Minimum Pickup LV | [6 empty] | 9
1.4 |  | Pengujian Waktu Kerja Diff Sisi LV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  | 0 | 0.03 | 3% |  | 9 | #DIV/0! | DIFF TRIP Ph R
|  | 2 |  | S |  | 0 | 0.031 | 3.1% |  | 9 | #DIV/0! | DIFF TRIP Ph S
|  | 3 |  | T |  | 0 | 0.031 | 3.1% |  | 9 | #DIV/0! | DIFF TRIP Ph T
|  | 4 |  | RST |  | 0 | 0.032 | 3.2% |  | 9 | #DIV/0! | DIFF TRIP Ph R-S-T
|  | Assessment Pengujian Waktu Kerja Diff Sisi LV | [6 empty] | 9
1.5 |  | Pengujian Arus Minimum Pickup Sisi TV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  |  |  | 0%
|  | 2 |  | S *) |  |  |  | 0%
|  | 3 |  | T *) |  |  |  | 0%
|  | 4 |  | RST |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian Arus Minimum Pickup TV | [6 empty] | 9
1.6 |  | Pengujian Waktu Kerja Diff Sisi TV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | S |  |  |  | 0% |  | 9 | #DIV/0!
|  | 3 |  | T |  |  |  | 0% |  | 9 | #DIV/0!
|  | 4 |  | RST |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian Waktu Kerja Diff Sisi TV | [6 empty] | 9
1.7 |  | Pengujian Arus Minimum Pickup REF
|  | NO |  | Item Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | REF HV |  | 0.12 | 0.119 | -0.8333% |  | 9 | -1 | REF HV TRIP
|  | 2 |  | REF LV |  | 0.152 | 0.152 | 0% |  | 9 | -1 | REF LV TRIP
|  | Assessment Pengujian Arus Minimum Pickup REF | [6 empty] | 9
1.8 |  | Pengujian Waktu Kerja REF
|  | NO |  | Item Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | REF HV |  | 0 | 0.039 | 3.9% |  | 9 | #DIV/0! | REF HV TRIP
|  | 2 |  | REF LV |  | 0 | 0.043 | 4.3% |  | 9 | #DIV/0! | REF LV TRIP
|  | Assessment Pengujian Waktu Kerja REF | [6 empty] | 9
1.9 |  | Pengujian Slope Diff
|  | NO |  | Item Pengujian |  | Nilai Idiff Acuan (In / pu / A)* | Nilai Idiff Hasil Uji (In / pu / A)* | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | S |  |  |  | 0% |  | 9 | #DIV/0!
|  | 3 |  | T |  |  |  | 0% |  | 9 | #DIV/0!
|  | 4 |  | RST |  | 6 | 6.003 | 0.05% |  | 9 | -1 | DIFF TRIP Ph R-S-T
*input hasil uji dengan error tertinggi
|  | Assessment Pengujian Slope Diff | [6 empty] | 9
1.10 |  | Pengujian 2nd & 5th Harmonic
|  | NO |  | Item Pengujian |  | Nilai Ixf/IDiff Acuan (%) | Nilai Ixf/IDiff Hasil Uji (%) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | 2nd Harm |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | 5th Harm |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian 2nd & 5th Harmonic | [6 empty] | 9
1.11 |  | Pengujian Zero Sequence Filtering
|  | Kondisi Fungsi Zero Sequnce Filtering |  |  |  | Hasil Pengujian (Trip / No Trip) | Assessment |  | Indikasi
|  | Non Aktif |  |  |  |  | 9
|  | Aktif |  |  |  |  | 9
|  | Assessment Pengujian Zero Sequence Filtering | [6 empty] | 9
1.12 |  | Evaluasi dan Keterangan
1.9 PENGUJIAN SLOPE MENGGUNAKAN LANGSUNG 3 FASA BERDASARKAN ALAT UJI
1.13 |  | Kesimpulan :
|  | Assessment Pengujian Individu Differential / REF | [6 empty] | 9
|  | *) | Pengujian pickup 1 fasa dilakukan dengan mempertimbangkan desain (BO Diff dan REF terpisah) dan keamanan (apabila diperlukan blocking fungsi REF). Pada pengujian pickup 1 fasa akan mendapat error yang besar.
Pelaksana | [8 empty] | Supervisi
1 | Riki H.
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [8 empty] | Ervan Jagi M W

## DIFF-REF MAIN B
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT |  | : | BEKASI
|  | ULTG |  | : | BEKASI
1.1 |  | Pengujian Arus Minimum Pickup DIFF Sisi HV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0.18 | 0.18 | 0% |  |  |  | DIFF TRIP PHASE R
|  | 2 |  | S *) |  | 0.18 | 0.18 | 0% |  |  |  | DIFF TRIP PHASE S
|  | 3 |  | T *) |  | 0.18 | 0.18 | 0% |  |  |  | DIFF TRIP PHASE T
|  | 4 |  | RST |  | 0.18 | 0.18 | 0% |  | 9 | -1 | DIFFERENSIAL TRIP RST
|  | Assessment Pengujian Arus Minimum Pickup HV | [6 empty] | 9
1.2 |  | Pengujian Waktu Kerja Diff Sisi HV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0 | 0.032 | 3.2% |  | 9 | #DIV/0! | DIFF TRIP PHASE R
|  | 2 |  | S *) |  | 0 | 0.031 | 3.1% |  | 9 | #DIV/0! | DIFF TRIP PHASE S
|  | 3 |  | T *) |  | 0 | 0.036 | 3.6% |  | 9 | #DIV/0! | DIFF TRIP PHASE T
|  | 4 |  | RST |  | 0 | 0.037 | 3.7% |  | 9 | #DIV/0! | DIFFERENSIAL TRIP RST
|  | Assessment Pengujian Waktu Kerja Diff Sisi HV | [6 empty] | 9
1.3 |  | Pengujian Arus Minimum Pickup Sisi LV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0.3 | 0.301 | 0.3333% |  |  |  | DIFF TRIP PHASE R
|  | 2 |  | S *) |  | 0.3 | 0.301 | 0.3333% |  |  |  | DIFF TRIP PHASE S
|  | 3 |  | T *) |  | 0.3 | 0.301 | 0.3333% |  |  |  | DIFF TRIP PHASE T
|  | 4 |  | RST |  | 0.3 | 0.301 | 0.3333% |  | 9 | -1 | DIFFERENSIAL TRIP RST
|  | Assessment Pengujian Arus Minimum Pickup LV | [6 empty] | 9
1.4 |  | Pengujian Waktu Kerja Diff Sisi LV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  | 0 | 0.03 | 3% |  | 9 | #DIV/0! | DIFF TRIP PHASE R
|  | 2 |  | S |  | 0 | 0.03 | 3% |  | 9 | #DIV/0! | DIFF TRIP PHASE S
|  | 3 |  | T |  | 0 | 0.029 | 2.9% |  | 9 | #DIV/0! | DIFF TRIP PHASE T
|  | 4 |  | RST |  | 0 | 0.034 | 3.4% |  | 9 | #DIV/0! | DIFFERENSIAL TRIP RST
|  | Assessment Pengujian Waktu Kerja Diff Sisi LV | [6 empty] | 9
1.5 |  | Pengujian Arus Minimum Pickup Sisi TV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  |  |  | 0%
|  | 2 |  | S *) |  |  |  | 0%
|  | 3 |  | T *) |  |  |  | 0%
|  | 4 |  | RST |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian Arus Minimum Pickup TV | [6 empty] | 9
1.6 |  | Pengujian Waktu Kerja Diff Sisi TV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | S |  |  |  | 0% |  | 9 | #DIV/0!
|  | 3 |  | T |  |  |  | 0% |  | 9 | #DIV/0!
|  | 4 |  | RST |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian Waktu Kerja Diff Sisi TV | [6 empty] | 9
1.7 |  | Pengujian Arus Minimum Pickup REF
|  | NO |  | Item Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | REF HV |  | 0.3 | 0.302 | 0.6667% |  | 9 | -1 | REF TRIP HV
|  | 2 |  | REF LV |  | 0.24 | 0.243 | 1.25% |  | 9 | -1 | REF TRIP LV
|  | Assessment Pengujian Arus Minimum Pickup REF | [6 empty] | 9
1.8 |  | Pengujian Waktu Kerja REF
|  | NO |  | Item Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | REF HV |  | 0 | 0.033 | 3.3% |  | 9 | #DIV/0! | REF TRIP HV
|  | 2 |  | REF LV |  | 0 | 0.033 | 3.3% |  | 9 | #DIV/0! | REF TRIP LV
|  | Assessment Pengujian Waktu Kerja REF | [6 empty] | 9
1.9 |  | Pengujian Slope Diff
|  | NO |  | Item Pengujian |  | Nilai Idiff Acuan (In / pu / A)* | Nilai Idiff Hasil Uji (In / pu / A)* | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | S |  |  |  | 0% |  | 9 | #DIV/0!
|  | 3 |  | T |  |  |  | 0% |  | 9 | #DIV/0!
|  | 4 |  | RST |  | 6.4 | 6.396 | -0.0625% |  | 9 | -1 | DIFFERENSIAL TRIP RST
*input hasil uji dengan error tertinggi
|  | Assessment Pengujian Slope Diff | [6 empty] | 9
1.10 |  | Pengujian 2nd & 5th Harmonic
|  | NO |  | Item Pengujian |  | Nilai Ixf/IDiff Acuan (%) | Nilai Ixf/IDiff Hasil Uji (%) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | 2nd Harm |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | 5th Harm |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian 2nd & 5th Harmonic | [6 empty] | 9
1.11 |  | Pengujian Zero Sequence Filtering
|  | Kondisi Fungsi Zero Sequnce Filtering |  |  |  | Hasil Pengujian (Trip / No Trip) | Assessment |  | Indikasi
|  | Non Aktif |  |  |  |  | 9
|  | Aktif |  |  |  |  | 9
|  | Assessment Pengujian Zero Sequence Filtering | [6 empty] | 9
1.12 |  | Evaluasi dan Keterangan
1.9 PENGUJIAN SLOPE MENGGUNAKAN LANGSUNG 3 FASA BERDASARKAN ALAT UJI
1.13 |  | Kesimpulan :
|  | Assessment Pengujian Individu Differential / REF | [6 empty] | 9
|  | *) | Pengujian pickup 1 fasa dilakukan dengan mempertimbangkan desain (BO Diff dan REF terpisah) dan keamanan (apabila diperlukan blocking fungsi REF). Pada pengujian pickup 1 fasa akan mendapat error yang besar.
Pelaksana | [8 empty] | Supervisi
1 | Riki H.
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [8 empty] | Ervan Jagi MW

## CCP MAIN A
PT. PLN (Persero) Unit Induk Transmisi Jawa Bagian Tengah
| UPT | : BEKASI
| ULTG | : BEKASI
HASIL UJI PROTEKSI CIRCULATING CURRENT PROTECTION (CCP) MAIN A
Merk | : ALSTOM |  |  | Ratio CT AB | : 2000/1 A
Type | : P643 |  |  | Ratio CT B | : 2000/1 A |  | :
Rating | : 1 A |  |  | Ratio CT LINE | : 2000/1 A
No.Serie | : 34136689/09/17 |  |  | Lokasi | : GITET MUARATAWAR |  | :
Thn Operasi | : 2025 |  |  | Bay | : IBT #1 |  | :
Alat Uji | : OMICRON 356 |  |  | Proteksi | : MAIN A |  | :
|  |  |  | Tanggal | : 07 APRIL 2026 |  | :
1. Pengujian Arus minimum Pick Up.
No. | Setting arus (I/IrObj) |  | Phase Injection Fault | Indication |  | Pick Up (Amp.)
1 | 1.2 |  | Phasa R | CCP Trip, Pickup Ph R |  | 1.129
2 | 1.2 |  | Phasa S | CCP Trip, Pickup Ph S |  | 1.129
3 | 1.2 |  | Phasa T | CCP Trip, Pickup Ph T |  | 1.129
2. Pengujian Waktu Kerja
No. | Setting Waktu (s) |  | Phase Injection Fault | Waktu Kerja (s)
1 | 0 |  | Phasa R | 0.023
2 | 0 |  | Phasa S | 0.024
3 | 0 |  | Phasa T | 0.026
3.Pengujian Fungsi PMT
No. | Injeksi | Phasa | Indikasi Relai | Indikasi Announ. dan Horn | PMT |  | Keterangan
1 | Internal Fault | R | CCP Trip, Pickup Ph R | CCP TRIP, RELAY PICKUP PHASE R | TRIP
2 | Internal Fault | S | CCP Trip, Pickup Ph S | CCP TRIP, RELAY PICKUP PHASE S | - |  | Trip Lockout
3 | Internal Fault | T | CCP Trip, Pickup Ph T | CCP TRIP, RELAY PICKUP PHASE T | - |  | Trip Lockout
4 | Eksternal Fault
5 | Eksternal Fault
6 | Eksternal Fault
catatan :
RELE KONDISI BAIK
PELAKSANA |  |  |  | SUPERVISI
1 | RIKI H
2 | RIZKY W. H.
3 | EDWAR D. V.
4
5
6 |  |  |  | ERVAN JAGI M W

## CCP MAIN B
PT. PLN (Persero) Unit Induk Transmisi Jawa Bagian Tengah
| UPT | : BEKASI
| ULTG | : BEKASI
HASIL UJI PROTEKSI CIRCULATING CURRENT PROTECTION (CCP) MAIN B
Merk | : GE MULTILIN |  |  | Ratio CT AB | : 2000/1 A
Type | :T60 |  |  | Ratio CT B | : 2000/1 A |  | :
Rating | : 1 A |  |  | Ratio CT LINE | : 2000/1 A
No.Serie | : ABHC17000989 |  |  | Lokasi | : GITET MUARATAWAR |  | :
Thn Operasi | : 2020 |  |  | Bay | : IBT #1 |  | :
Alat Uji | : OMICRON CMC356 |  |  | Proteksi | : MAIN B |  | :
|  |  |  | Tanggal | : 7 APRIL 2026 |  | :
1. Pengujian Arus minimum Pick Up.
No. | Setting arus (PU) |  | Phase Injection Fault | Indication |  | Pick Up (Amp.)
1 | 0.2 |  | Phasa R | TRIP, PHASA R |  | 0.201
2 | 0.2 |  | Phasa S | TRIP, PHASA S |  | 0.201
3 | 0.2 |  | Phasa T | TRIP, PHASA T |  | 0.201
2. Pengujian Waktu Kerja
No. | Setting Waktu (s) |  | Phase Injection Fault | Waktu Kerja (s)
1 | 0 |  | Phasa R | 0.035
2 | 0 |  | Phasa S | 0.037
3 | 0 |  | Phasa T | 0.035
3.Pengujian Fungsi PMT
No. | Injeksi | Phasa | Indikasi Relai | Indikasi Announ. dan Horn | PMT |  | Keterangan
1 | Internal Fault | R | TRIP, PHASA R | CCP TRIP, RELAY PICKUP PHASE R | - |  | Trip Lockout
2 | Internal Fault | S | TRIP, PHASA S | CCP TRIP, RELAY PICKUP PHASE S | TRIP
3 | Internal Fault | T | TRIP, PHASA T | CCP TRIP, RELAY PICKUP PHASE T | - |  | Trip Lockout
4 | Eksternal Fault
5 | Eksternal Fault
6 | Eksternal Fault
catatan :
RELE KONDISI BAIK
PELAKSANA |  |  |  | SUPERVISI
1 | RIKI H.
2 | RIZKY W. H.
3 | EDWAR D. V.
4
5
6 |  |  |  | ERVAN JAGI MW

## OCR-GFR HV
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
2 |  | Setting OCR dan GFR HV
|  | Setting Arus Pickup OCR |  |  |  |  | : | 0.7 |  |  | A
|  | Setting TMS OCR |  |  |  |  | : | 0.34
|  | Setting Arus Pickup GFR |  |  |  |  | : | 0.46 |  |  | A
|  | Setting TMS GFR |  |  |  |  | : | 0.36
2.1 |  | Pengujian Arus Pickup dan Dropoff OCR/GFR HV
|  | Jenis Pengujian |  |  | Parameter |  |  |  | OCR R |  |  | OCR S |  |  | OCR T |  |  | GFR
|  | Pickup |  |  | Hasil Uji (A) |  |  |  | 0.701 |  |  | 0.701 |  |  | 0.701 |  |  | 0.461
[5 empty] | % Error |  |  |  | 0.1429% |  |  | 0.1429% |  |  | 0.1429% |  |  | 0.2174% | 0
[5 empty] | Assessment |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 | 0
|  | Dropoff |  |  | Hasil Uji (A) |  |  |  | 0.685 |  |  | 0.685 |  |  | 0.685 |  |  | 0.45
[5 empty] | % Rasio DO/PU |  |  |  | 97.72% |  |  | 97.72% |  |  | 97.72% |  |  | 97.61% | 0
[5 empty] | Assessment |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 | 0
|  | Assessment Pengujian Pickup dan Dropoff | [10 empty] | 9
2.2 |  | Pengujian Karakteristik Waktu Kerja OCR dan GFR HV
|  | Poin Pengujian |  |  | Parameter |  |  |  | 1.5 x Iset |  |  | 2.0 x Iset |  |  | 2.5 x Iset |  |  | 3.0 x Iset
|  | OCR Fasa R |  |  | Arus Injeksi (A) |  |  |  | 1.05 |  |  | 1.4 |  |  | 1.75 |  |  | 2.1
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 5.846 |  |  | 3.4099 |  |  | 2.5737 |  |  | 2.1427
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.431 |  |  | - |  |  | 2.161
[5 empty] | % Error |  |  |  | 0% |  |  | 0.6197% |  |  | 0% |  |  | 0.8561%
|  | OCR Fasa S |  |  | Arus Injeksi (A) |  |  |  | 1.05 |  |  | 1.4 |  |  | 1.75 |  |  | 2.1 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 5.846 |  |  | 3.4099 |  |  | 2.5737 |  |  | 2.1427
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.434 |  |  | - |  |  | 2.165
[5 empty] | % Error |  |  |  | 0% |  |  | 0.7077% |  |  | 0% |  |  | 1.043%
|  | OCR Fasa T |  |  | Arus Injeksi (A) |  |  |  | 1.05 |  |  | 1.4 |  |  | 1.75 |  |  | 2.1
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 5.846 |  |  | 3.4099 |  |  | 2.5737 |  |  | 2.1427
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.43 |  |  | - |  |  | 2.162
[5 empty] | % Error |  |  |  | 0% |  |  | 0.5904% |  |  | 0% |  |  | 0.9028%
|  | GFR |  |  | Arus Injeksi (A) |  |  |  | 0.69 |  |  | 0.92 |  |  | 1.15 |  |  | 1.38 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 6.1899 |  |  | 3.6104 |  |  | 2.7251 |  |  | 2.2687
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.63 |  |  | - |  |  | 2.287
[5 empty] | % Error |  |  |  | 0% |  |  | 0.5415% |  |  | 0% |  |  | 0.8068%
|  | Kalkulasi Error Terbesar | [6 empty] | 0% |  |  | 0.7077% |  |  | 0% |  |  | 1.043%
|  | Hasil Asesmen | [6 empty] | 9 |  |  | 9 |  |  | 9 |  |  | 9
|  | Assessment Pengujian Karakteristik Waktu Kerja | [10 empty] | 9
2.3 |  | Pengujian Arus Kerja OCR Moment/Highset HV
|  | NO | Item Pengujian |  |  | Setting Arus (Ampere) |  |  |  | Hasil Uji Pickup Arus (Ampere) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 |  |  | 6.7 |  |  |  | 6.7 |  | 0% |  | 9 |  | -1 | OCR TRIP
|  | Assessment Pengujian Arus Kerja OCR Moment | [10 empty] | 9
2.4 |  | Pengujian Waktu Kerja OCR Moment/Highset HV
|  | NO | Item Pengujian |  |  | Setting Waktu Kerja (s) |  |  |  | Hasil Uji Waktu Kerja (s) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 |  |  | 0.1 |  |  |  | 0.126 |  | 2.6% |  | 9 |  | -1 | OCR TRIP
|  | Assessment Pengujian Waktu Kerja OCR Moment/Highset HV | [10 empty] | 9
2.5 |  | Evaluasi dan Keterangan
OCR dan GFR sisi 500 kV (HV)
2.6 |  | Kesimpulan :
|  | Assessment Pengujian Individu OCR/GFR HV | [10 empty] | 9
Pelaksana | [11 empty] | Supervisi
1 | Riki H
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [11 empty] | Ervan Jagi M W

## OCR-GFR LV
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
3 |  | Setting OCR dan GFR LV
|  | Setting Arus Pickup OCR |  |  |  |  | : | 1.2 |  |  | A
|  | Setting TMS OCR |  |  |  |  | : | 0.33
|  | Setting Arus Pickup GFR |  |  |  |  | : | 0.2 |  |  | A
|  | Setting TMS GFR |  |  |  |  | : | 0.8
3.1 |  | Pengujian Arus Pickup dan Dropoff OCR/GFR LV
|  | Jenis Pengujian |  |  | Parameter |  |  |  | OCR R |  |  | OCR S |  |  | OCR T |  |  | GFR
|  | Pickup |  |  | Hasil Uji (A) |  |  |  | 1.197 |  |  | 1.197 |  |  | 1.197 |  |  | 0.2
[5 empty] | % Error |  |  |  | -0.25% |  |  | -0.25% |  |  | -0.25% |  |  | 0% | 0
[5 empty] | Assessment |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 | 0
|  | Dropoff |  |  | Hasil Uji (A) |  |  |  | 1.131 |  |  | 1.131 |  |  | 1.131 |  |  | 0.19
[5 empty] | % Rasio DO/PU |  |  |  | 94.49% |  |  | 94.49% |  |  | 94.49% |  |  | 95% | 3
[5 empty] | Assessment |  |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 9 | 0
|  | Assessment Pengujian Pickup dan Dropoff | [10 empty] | 6
3.2 |  | Pengujian Karakteristik Waktu Kerja OCR dan GFR LV
|  | Poin Pengujian |  |  | Parameter |  |  |  | 1.5 x Iset |  |  | 2.0 x Iset |  |  | 2.5 x Iset |  |  | 3.0 x Iset
|  | OCR Fasa R |  |  | Arus Injeksi (A) |  |  |  | 1.8 |  |  | 2.4 |  |  | 3 |  |  | 3.6
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 5.6741 |  |  | 3.3096 |  |  | 2.498 |  |  | 2.0796
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.319 |  |  | - |  |  | 2.105
[5 empty] | % Error |  |  |  | 0% |  |  | 0.2847% |  |  | 0% |  |  | 1.22%
|  | OCR Fasa S |  |  | Arus Injeksi (A) |  |  |  | 1.8 |  |  | 2.4 |  |  | 3 |  |  | 3.6 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 5.6741 |  |  | 3.3096 |  |  | 2.498 |  |  | 2.0796
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.314 |  |  | - |  |  | 2.103
[5 empty] | % Error |  |  |  | 0% |  |  | 0.1336% |  |  | 0% |  |  | 1.123%
|  | OCR Fasa T |  |  | Arus Injeksi (A) |  |  |  | 1.8 |  |  | 2.4 |  |  | 3 |  |  | 3.6
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 5.6741 |  |  | 3.3096 |  |  | 2.498 |  |  | 2.0796
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 3.319 |  |  | - |  |  | 2.104
[5 empty] | % Error |  |  |  | 0% |  |  | 0.2847% |  |  | 0% |  |  | 1.171%
|  | GFR |  |  | Arus Injeksi (A) |  |  |  | 0.3 |  |  | 0.4 |  |  | 0.5 |  |  | 0.6 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 13.7554 |  |  | 8.0232 |  |  | 6.0558 |  |  | 5.0415
[5 empty] | Hasil Uji (s) |  |  |  | - |  |  | 8.019 |  |  | - |  |  | 5.057
[5 empty] | % Error |  |  |  | 0% |  |  | -0.05262% |  |  | 0% |  |  | 0.3066%
|  | Kalkulasi Error Terbesar | [6 empty] | 0% |  |  | 0.2847% |  |  | 0% |  |  | 1.22%
|  | Hasil Asesmen | [6 empty] | 9 |  |  | 9 |  |  | 9 |  |  | 9
|  | Assessment Pengujian Karakteristik Waktu Kerja | [10 empty] | 9
3.3 |  | Pengujian Arus Kerja OCR Moment/Highset LV
|  | NO | Item Pengujian |  |  | Setting Arus (Ampere) |  |  |  | Hasil Uji Pickup Arus (Ampere) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 2 | OCR HS2 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 3 | GFR HS1 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 4 | GFR HS2 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | Assessment Pengujian Arus Kerja OCR Moment | [10 empty] | 9
3.4 |  | Pengujian Waktu Kerja OCR Moment/Highset LV
|  | NO | Item Pengujian |  |  | Setting Waktu Kerja (s) |  |  |  | Hasil Uji Waktu Kerja (s) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 2 | OCR HS2 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 3 | GFR HS1 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 4 | GFR HS2 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | Assessment Pengujian Waktu Kerja OCR Moment/Highset LV | [10 empty] | 9
3.5 |  | Evaluasi dan Keterangan
OCR dan GFR sisi 150 kV (LV)
3.6 |  | Kesimpulan :
|  | Assessment Pengujian Individu OCR/GFR LV | [10 empty] | 6
Pelaksana | [11 empty] | Supervisi
1 | Riki H.
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [11 empty] | Ervan Jagi M W

## NVDR-OV
PT. PLN (Persero) Unit Induk Transmisi Jawa Bagian Tengah
|  |  | UPT |  | : BEKASI
|  |  | ULTG |  | : BEKASI
4.3 HASIL UJI PROTEKSI UNDER/OVER VOLTAGE RELAY
Merk |  |  |  |  | : ALSTOM | [7 empty] | Ratio PT |  |  | : | 66000/100 V
Type |  |  |  |  | : P143 | [7 empty] | Lokasi |  |  | : | GITET MUARATAWAR
No. Serie |  |  |  |  | : 34193362/08/17 | [7 empty] | Bay |  |  | : | IBT #1 SISI LV
Rating |  |  |  |  | : 100 V | [7 empty] | Alat Uji |  |  | : | OMICRON 364
Karakteristik |  |  |  |  | : | [7 empty] | Tanggal |  |  | : | 2026-04-07
1 | ARUS KERJA MINIMUM DAN KEMBALI
| FASA | [9 empty] | NVDR |  |  |  | OVER VOLT |  |  | KETERANGAN
| TEGANGAN NOMINAL | [5 empty] | (Vn) |  | Volt |  | 100 |  |  |  | 100
| SETTING STAGE 1 | [5 empty] | (Vs) |  | Volt |  | 12.73 |  |  |  | 73.63 |  |  | ALARM
| SETTING STAGE 2 | [5 empty] | (Vs) |  | Volt |  | 18.18 |  |  |  | 91.81 |  |  | TRIP
| TEGANGAN KERJA T1 | [5 empty] | (Vp) |  | Volt |  | 12.33 |  |  |  | 73.7 |  |  | PICKUP
| TEGANGAN KERJA T2 | [5 empty] | (Vp) |  | Volt |  | 18.5 |  |  |  | 91.83 |  |  | TRIP
| WAKTU KERJA STAGE 1 | [5 empty] | (t) |  | s |  | 5.023 |  |  |  | 5.09 |  |  | T alarm
| WAKTU KERJA STAGE 2 | [5 empty] | (t) |  | s |  | 2.527 |  |  |  | 2.502 |  |  | T trip
2 | SETTING AKHIR RELE
| POSISI SETTING | [8 empty] | POSISI SETTING | [8 empty] | KETERANGAN
| VOLTAGE |  |  | Vn |  | Vs |  | Vs |  | VOLTAGE |  | Vn |  | Vs |  |  | Vs
|  |  |  | (V) |  | (V) |  | (V) |  |  |  | (V) |  | (V) |  |  | (V)
| NVDR |  |  | 100 |  | 12.73 |  | 18.18 |  | OVER VOLT |  | 100 |  | 73.63 |  |  | 91.83 |  | SESUAI
|  |  |  | 100 |  | ALARM |  | TRIP |  |  |  | 100 |  | ALARM |  |  | TRIP
| Time Result |  |  |  |  | 5 s |  | 2,5 s |  | Time Result |  |  |  | 5 s |  |  | 2,5 s |  | SESUAI
5 | PENGUJIAN FUNGSI
| NO |  | INJEKSI |  |  |  | INDIKASI | [5 empty] | PMT |  |  |  | KETERANGAN
| 1 |  | NVDR |  |  |  | ALARM; NVDR | [5 empty] | NO TRIP |  |  |  | SESUAI
| 2 |  | NVDR |  |  |  | ALARM; TRIP; NVDR; LOCKOUT OP | [5 empty] | TRIP |  |  |  | SESUAI
| 3 |  | OVR |  |  |  | ALARM; OVR | [5 empty] | NO TRIP |  |  |  | SESUAI
| 4 |  | OVR |  |  |  | ALARM; TRIP; OVR; LOCKOUT OP | [5 empty] | TRIP |  |  |  | SESUAI
6 | CATATAN
untuk fungsi Trip pada relay NDVR pada rangkaian trip masih di block dengan open
blade
[5 empty] | PELAKSANA | [11 empty] | SUPERVISI
| 1. | RIKI H
| 2. | EDWAR DENDY
| 3. | RIZKY WIRA
4
5
| 6 | [10 empty] | ERVAN JAGI M W

## UJI FUNGSI
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT |  | : | BEKASI
|  | ULTG |  | : | BEKASI
5.1 |  | Pengujian Fungsi Main Proteksi
|  | Fungsi Proteksi |  |  |  | Pengujian Fasa | Kinerja Acuan |  |  |  | Hasil Uji *) | Assessment | Indikasi Relai, Annunciator & Lockout
|  | DIFF |  |  |  | RST HV | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | TRIP, DIFF PH ABC &K401
|  | DIFF |  |  |  | RST LV | Trip 3 fasa, Lockout, PMT HV dan LV Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  | OK | 9 | TRIP, DIFF PH ABC&K401
|  | REF HV |  |  |  | HV | Trip 3 fasa, Lockout, PMT HV dan LV Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  | OK | 9 | TRIP, REF HV&K401
|  | REF LV |  |  |  | LV | Trip 3 fasa, Lockout, PMT HV dan LV Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  | OK | 9 | TRIP, REF LV&K401
|  | *) | Jika hasil uji sesuai, input hanya tulisan OK, jika tidak sesuai maka tulis sesuai hasil pengujian
|  | Assessment Pengujian Fungsi Main Proteksi | [7 empty] | 9
5.2 |  | Pengujian Fungsi Backup Proteksi
|  | Fungsi Proteksi |  |  |  | Pengujian Fasa | Kinerja Acuan |  |  |  | Hasil Uji *) | Assessment | Indikasi Relai, Annunciator & Lockout
|  | OCR HV |  |  |  | RST | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | TRIP ABC, I> &K402
|  | OCR HV Moment |  |  |  | RST | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | TRIP, I>> &K402
|  | GFR HV |  |  |  | N | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | TRIP, IO> &K402
|  | OCR LV |  |  |  | RST | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | TRIP ABC, 50/51 >&K403,K404
|  | OCR LV HS1 |  |  |  | RST | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | OCR LV HS2 |  |  |  | RST | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | GFR LV |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | 50/51N>&K403,K404
|  | GFR LV HS1 |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | GFR LV HS2 |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | SBEF |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | *) | Jika hasil uji sesuai, input hanya tulisan OK, jika tidak sesuai maka tulis sesuai hasil pengujian
|  | Assessment Pengujian Fungsi Backup Proteksi | [7 empty] | 9
5.3 |  | Evaluasi dan Keterangan
PENGUJIAN FUNGSI PMT SESUAI DENGAN FUNGSINYA
5.4 |  | Kesimpulan :
|  | Assessment Pengujian Fungsi | [7 empty] | 9
Pelaksana | [8 empty] | Supervisi
1 | RIZKY WIRA H
2 | EDWAR DENDY
3 | RIKI HARDIANTO
4
5 | [8 empty] | ERVAN JAGI M.W