## COVER
LAPORAN TEKNIK PEMELIHARAAN RUTIN
SISTEM PROTEKSI BAY TRAFO
PT PLN (PERSERO) UNIT INDUK TRANSMISI
JAWA BAGIAN TENGAH
|  |  |  | UPT | : | BEKASI
|  |  |  | ULTG | : | BEKASI
|  |  |  | GI / GITET | : | CIKARANG 150 KV
|  |  |  | BAY | : | TRAFO #1
|  |  |  | TANGGAL | : | 24 JUNI 2026
| Spesifikasi Relai Proteksi Utama | [7 empty] | Spesifikasi Relai Proteksi OCR/GFR 150 kV
| Merk Relai |  | : | ABB |  |  |  |  | Merk Relai | : | ABB
| Tipe Relai |  | : | RET650 |  |  |  |  | Tipe Relai | : | REF615
| No Serie |  | : | T1645034 |  |  |  |  | No Serie | : | IVHR91309422
| Tahun Operasi |  | : | [5 empty] | Tahun Operasi | :
| Rasio CT HV |  | : | 300/1 A |  |  |  |  | Rasio CT | : | 300/1 A
| Rasio CTN HV |  | : | 300/1 A |  |  |  |  | Alat Uji | : | MEGGER SMRT46
| Rasio CT LV |  | : | 2000/5 A
| Rasio CTN LV |  | : | 2000/5 A |  |  |  |  | Spesifikasi Relai Proteksi OCR/GFR 20 kV
| Alat Uji |  | : | MEGGER SMRT46 |  |  |  |  | Merk Relai | : | ABB
[9 empty] | Tipe Relai | : | REF615
| Spesifikasi Relai Proteksi SBEF | [7 empty] | No Serie | : | 1VHK91309404
| Merk Relai |  | : | ABB |  |  |  |  | Tahun Operasi | :
| Tipe Relai |  | : | REF615 |  |  |  |  | Rasio CT | : | 2000/1 A
| No Serie |  | : | 1VHK91309404 |  |  |  |  | Alat Uji | : | MEGGER SMRT46
| Tahun Operasi |  | :
| Rasio CT |  | : | 1000/5 A
| Alat Uji |  | : | MEGGER SMRT46
KESIMPULAN HASIL PEMELIHARAAN RUTIN SISTEM PROTEKSI
|  |  | Hasil Assessment Proteksi |  |  |  | 6
Pelaksana | [7 empty] | Supervisi
1 | Riki H
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [7 empty] | ERVAN JAGI M W
PT PLN (Persero) Unit Induk Transmisi Jawa Bagian Tengah
Sub Bidang Pemeliharaan Proteksi & meter
Tahun 2024

## DIFF TRAFO
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT |  | : | BEKASI
|  | ULTG |  | : | BEKASI
1.1 |  | Pengujian Arus Minimum Pickup DIFF Sisi HV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0.3 | 0.3 | 0% |  |  |  | Diff Trip, Start L1
|  | 2 |  | S *) |  | 0.3 | 0.3 | 0% |  |  |  | Diff Trip, Start L2
|  | 3 |  | T *) |  | 0.3 | 0.3 | 0% |  |  |  | Diff Trip, Start L3
|  | 4 |  | RST |  | 0.3 | 0.294 | -2% |  | 9 | -1 | Diff Trip, Start L1-L2-L3
|  | Assessment Pengujian Arus Minimum Pickup HV | [6 empty] | 9
1.2 |  | Pengujian Waktu Kerja Diff Sisi HV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0 | 0.024 | 2.4% |  | 9 | #DIV/0! | Diff Trip, Start L1
|  | 2 |  | S *) |  | 0 | 0.028 | 2.8% |  | 9 | #DIV/0! | Diff Trip, Start L2
|  | 3 |  | T *) |  | 0 | 0.025 | 2.5% |  | 9 | #DIV/0! | Diff Trip, Start L3
|  | 4 |  | RST |  | 0 | 0.024 | 2.4% |  | 9 | #DIV/0! | Diff Trip, Start L1-L2-L3
|  | Assessment Pengujian Waktu Kerja Diff Sisi HV | [6 empty] | 9
1.3 |  | Pengujian Arus Minimum Pickup Sisi LV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  | 0.3 | 0.303 | 1% |  |  |  | Diff Trip, Start L1
|  | 2 |  | S *) |  | 0.3 | 0.3 | 0% |  |  |  | Diff Trip, Start L2
|  | 3 |  | T *) |  | 0.3 | 0.3 | 0% |  |  |  | Diff Trip, Start L3
|  | 4 |  | RST |  | 0.3 | 0.33 | 10% |  | 6 | -1 | Diff Trip, Start L1-L2-L3
|  | Assessment Pengujian Arus Minimum Pickup LV | [6 empty] | 6
1.4 |  | Pengujian Waktu Kerja Diff Sisi LV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  | 0 | 0.024 | 2.4% |  | 9 | #DIV/0! | Diff Trip, Start L1
|  | 2 |  | S |  | 0 | 0.028 | 2.8% |  | 9 | #DIV/0! | Diff Trip, Start L2
|  | 3 |  | T |  | 0 | 0.025 | 2.5% |  | 9 | #DIV/0! | Diff Trip, Start L3
|  | 4 |  | RST |  | 0 | 0.024 | 2.4% |  | 9 | #DIV/0! | Diff Trip, Start L1-L2-L3
|  | Assessment Pengujian Waktu Kerja Diff Sisi LV | [6 empty] | 9
1.5 |  | Pengujian Arus Minimum Pickup Sisi TV
|  | NO |  | Fasa Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R *) |  |  |  | 0%
|  | 2 |  | S *) |  |  |  | 0%
|  | 3 |  | T *) |  |  |  | 0%
|  | 4 |  | RST |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian Arus Minimum Pickup TV | [6 empty] | 9
1.6 |  | Pengujian Waktu Kerja Diff Sisi TV
|  | NO |  | Fasa Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | S |  |  |  | 0% |  | 9 | #DIV/0!
|  | 3 |  | T |  |  |  | 0% |  | 9 | #DIV/0!
|  | 4 |  | RST |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian Waktu Kerja Diff Sisi TV | [6 empty] | 9
1.7 |  | Pengujian Arus Minimum Pickup REF
|  | NO |  | Item Pengujian |  | Setting Arus (Ampere) | Hasil Uji Pickup Arus (Ampere) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | REF HV |  | 0.154 | 0.156 | 1.299% |  | 9 | -1 | HV REF Trip
|  | 2 |  | REF LV |  | 0.866 | 0.868 | 0.2309% |  | 9 | -1 | LV REF Trip
|  | Assessment Pengujian Arus Minimum Pickup REF | [6 empty] | 9
1.8 |  | Pengujian Waktu Kerja REF
|  | NO |  | Item Pengujian |  | Setting Waktu (s) | Hasil Pengujian (s) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | REF HV |  | 0 | 0.033 | 3.3% |  | 9 | #DIV/0! | HV REF Trip
|  | 2 |  | REF LV |  | 0 | 0.031 | 3.1% |  | 9 | #DIV/0! | LV REF Trip
|  | Assessment Pengujian Waktu Kerja REF | [6 empty] | 9
1.9 |  | Pengujian Slope Diff
|  | NO |  | Item Pengujian |  | Nilai Idiff Acuan (In / pu / A)* | Nilai Idiff Hasil Uji (In / pu / A)* | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | R |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | S |  |  |  | 0% |  | 9 | #DIV/0!
|  | 3 |  | T |  |  |  | 0% |  | 9 | #DIV/0!
|  | 4 |  | RST |  | 0.8 | 0.82 | 2.5% |  | 9 | -1 | Diff Trip, Start L1-L2-L3
*input hasil uji dengan error tertinggi
|  | Assessment Pengujian Slope Diff | [6 empty] | 9
1.10 |  | Pengujian 2nd & 5th Harmonic
|  | NO |  | Item Pengujian |  | Nilai Ixf/IDiff Acuan (%) | Nilai Ixf/IDiff Hasil Uji (%) | Nilai Error (Persen) |  | Assessment |  | Indikasi
|  | 1 |  | 2nd Harm |  |  |  | 0% |  | 9 | #DIV/0!
|  | 2 |  | 5th Harm |  |  |  | 0% |  | 9 | #DIV/0!
|  | Assessment Pengujian 2nd & 5th Harmonic | [6 empty] | 9
1.11 |  | Pengujian Zero Sequence Filtering
|  | Kondisi Fungsi Zero Sequnce Filtering |  |  |  | Hasil Pengujian (Trip / No Trip) | Assessment |  | Indikasi
|  | Non Aktif |  |  |  |  | 9
|  | Aktif |  |  |  |  | 9
|  | Assessment Pengujian Zero Sequence Filtering | [6 empty] | 9
1.12 |  | Evaluasi dan Keterangan
1.1 SETTING DAN HASIL UJI DALAM SATUAN PU 1.3 SETTING DAN HASIL UJI DALAM SATUAN PU 1.9 PENGUJIAN SLOPE MENGGUNAKAN LANGSUNG 3 FASA BERDASARKAN ALAT UJI
1.13 |  | Kesimpulan :
|  | Assessment Pengujian Individu Differential / REF | [6 empty] | 6
|  | *) | Pengujian pickup 1 fasa dilakukan dengan mempertimbangkan desain (BO Diff dan REF terpisah) dan keamanan (apabila diperlukan blocking fungsi REF). Pada pengujian pickup 1 fasa akan mendapat error yang besar.
Pelaksana | [8 empty] | Supervisi
1 | Riki H
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [8 empty] | ERVAN JAGI M W

## OCR-GFR HV
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
2 |  | Setting OCR dan GFR HV
|  | Setting Arus Pickup OCR |  |  |  |  | : | 0.92 |  |  | A
|  | Setting TMS OCR |  |  |  |  | : | 0.36
|  | Setting Arus Pickup GFR |  |  |  |  | : | 0.385 |  |  | A
|  | Setting TMS GFR |  |  |  |  | : | 0.59
2.1 |  | Pengujian Arus Pickup dan Dropoff OCR/GFR HV
|  | Jenis Pengujian |  |  | Parameter |  |  |  | OCR R |  |  | OCR S |  |  | OCR T |  |  | GFR
|  | Pickup |  |  | Hasil Uji (A) |  |  |  | 0.938 |  |  | 0.929 |  |  | 0.938 |  |  | 0.397
[5 empty] | % Error |  |  |  | 1.957% |  |  | 0.9783% |  |  | 1.957% |  |  | 3.117% | 0
[5 empty] | Assessment |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 | 0
|  | Dropoff |  |  | Hasil Uji (A) |  |  |  | 0.865 |  |  | 0.865 |  |  | 0.874 |  |  | 0.358
[5 empty] | % Rasio DO/PU |  |  |  | 92.22% |  |  | 93.11% |  |  | 93.18% |  |  | 90.18% | 4
[5 empty] | Assessment |  |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 6 | 0
|  | Assessment Pengujian Pickup dan Dropoff | [10 empty] | 6
2.2 |  | Pengujian Karakteristik Waktu Kerja OCR dan GFR HV
|  | Poin Pengujian |  |  | Parameter |  |  |  | 1.5 x Iset |  |  | 2.0 x Iset |  |  | 2.5 x Iset |  |  | 3.0 x Iset
|  | OCR Fasa R |  |  | Arus Injeksi (A) |  |  |  | 1.38 |  |  | 1.84 |  |  | 2.3 |  |  | 2.76
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 6.1899 |  |  | 3.6104 |  |  | 2.7251 |  |  | 2.2687
[5 empty] | Hasil Uji (s) |  |  |  | 6.264 |  |  | 3.629 |  |  | 2.744 |  |  | 2.285
[5 empty] | % Error |  |  |  | 1.197% |  |  | 0.5138% |  |  | 0.6937% |  |  | 0.7187%
|  | OCR Fasa S |  |  | Arus Injeksi (A) |  |  |  | 1.38 |  |  | 1.84 |  |  | 2.3 |  |  | 2.76 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 6.1899 |  |  | 3.6104 |  |  | 2.7251 |  |  | 2.2687
[5 empty] | Hasil Uji (s) |  |  |  | 6.264 |  |  | 3.627 |  |  | 2.743 |  |  | 2.281
[5 empty] | % Error |  |  |  | 1.197% |  |  | 0.4584% |  |  | 0.657% |  |  | 0.5424%
|  | OCR Fasa T |  |  | Arus Injeksi (A) |  |  |  | 1.38 |  |  | 1.84 |  |  | 2.3 |  |  | 2.76
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 6.1899 |  |  | 3.6104 |  |  | 2.7251 |  |  | 2.2687
[5 empty] | Hasil Uji (s) |  |  |  | 6.263 |  |  | 3.63 |  |  | 2.743 |  |  | 2.284
[5 empty] | % Error |  |  |  | 1.181% |  |  | 0.5415% |  |  | 0.657% |  |  | 0.6746%
|  | GFR |  |  | Arus Injeksi (A) |  |  |  | 0.5775 |  |  | 0.77 |  |  | 0.9625 |  |  | 1.155 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 10.1446 |  |  | 5.9171 |  |  | 4.4661 |  |  | 3.7181
[5 empty] | Hasil Uji (s) |  |  |  | 10.525 |  |  | 6.05 |  |  | 4.539 |  |  | 3.779
[5 empty] | % Error |  |  |  | 3.75% |  |  | 2.246% |  |  | 1.632% |  |  | 1.637%
|  | Kalkulasi Error Terbesar | [6 empty] | 3.75% |  |  | 2.246% |  |  | 1.632% |  |  | 1.637%
|  | Hasil Asesmen | [6 empty] | 9 |  |  | 9 |  |  | 9 |  |  | 9
|  | Assessment Pengujian Karakteristik Waktu Kerja | [10 empty] | 9
2.3 |  | Pengujian Arus Kerja OCR Moment/Highset HV
|  | NO | Item Pengujian |  |  | Setting Arus (Ampere) |  |  |  | Hasil Uji Pickup Arus (Ampere) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 |  |  | 7.6 |  |  |  | 7.6 |  | 0% |  | 9 |  | -1 | PHHPTOC1 OPERATE
|  | Assessment Pengujian Arus Kerja OCR Moment | [10 empty] | 9
2.4 |  | Pengujian Waktu Kerja OCR Moment/Highset HV
|  | NO | Item Pengujian |  |  | Setting Waktu Kerja (s) |  |  |  | Hasil Uji Waktu Kerja (s) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 |  |  | 0.04 |  |  |  | 0.062 |  | 2.2% |  | 9 |  | -1 | PHHPTOC1 OPERATE
|  | Assessment Pengujian Waktu Kerja OCR Moment/Highset HV | [10 empty] | 9
2.5 |  | Evaluasi dan Keterangan
2.6 |  | Kesimpulan :
|  | Assessment Pengujian Individu OCR/GFR HV | [10 empty] | 6
Pelaksana | [11 empty] | Supervisi
1 | Riki H
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [11 empty] | ERVAN JAGI M W

## OCR-GFR LV
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
3 |  | Setting OCR dan GFR LV
|  | Setting Arus Pickup OCR |  |  |  |  | : | 5.2 |  |  | A
|  | Setting TMS OCR |  |  |  |  | : | 0.24
|  | Setting Arus Pickup GFR |  |  |  |  | : | 0.85 |  |  | A
|  | Setting TMS GFR |  |  |  |  | : | 0.15
3.1 |  | Pengujian Arus Pickup dan Dropoff OCR/GFR LV
|  | Jenis Pengujian |  |  | Parameter |  |  |  | OCR R |  |  | OCR S |  |  | OCR T |  |  | GFR
|  | Pickup |  |  | Hasil Uji (A) |  |  |  | 5.252 |  |  | 5.252 |  |  | 5.252 |  |  | 0.85
[5 empty] | % Error |  |  |  | 1% |  |  | 1% |  |  | 1% |  |  | 0% | 0
[5 empty] | Assessment |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9 | 0
|  | Dropoff |  |  | Hasil Uji (A) |  |  |  | 4.836 |  |  | 4.836 |  |  | 4.836 |  |  | 0.799
[5 empty] | % Rasio DO/PU |  |  |  | 92.08% |  |  | 92.08% |  |  | 92.08% |  |  | 94% | 4
[5 empty] | Assessment |  |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 6 | 0
|  | Assessment Pengujian Pickup dan Dropoff | [10 empty] | 6
3.2 |  | Pengujian Karakteristik Waktu Kerja OCR dan GFR LV
|  | Poin Pengujian |  |  | Parameter |  |  |  | 1.5 x Iset |  |  | 2.0 x Iset |  |  | 2.5 x Iset |  |  | 3.0 x Iset
|  | OCR Fasa R |  |  | Arus Injeksi (A) |  |  |  | 7.8 |  |  | 10.4 |  |  | 13 |  |  | 15.6
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 4.1266 |  |  | 2.407 |  |  | 1.8167 |  |  | 1.5125
[5 empty] | Hasil Uji (s) |  |  |  | 4.173 |  |  | 2.421 |  |  | 1.827 |  |  | 1.524
[5 empty] | % Error |  |  |  | 1.124% |  |  | 0.583% |  |  | 0.5653% |  |  | 0.7628%
|  | OCR Fasa S |  |  | Arus Injeksi (A) |  |  |  | 7.8 |  |  | 10.4 |  |  | 13 |  |  | 15.6 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 4.1266 |  |  | 2.407 |  |  | 1.8167 |  |  | 1.5125
[5 empty] | Hasil Uji (s) |  |  |  | 4.177 |  |  | 2.422 |  |  | 1.831 |  |  | 1.524
[5 empty] | % Error |  |  |  | 1.221% |  |  | 0.6246% |  |  | 0.7854% |  |  | 0.7628%
|  | OCR Fasa T |  |  | Arus Injeksi (A) |  |  |  | 7.8 |  |  | 10.4 |  |  | 13 |  |  | 15.6
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 4.1266 |  |  | 2.407 |  |  | 1.8167 |  |  | 1.5125
[5 empty] | Hasil Uji (s) |  |  |  | 4.174 |  |  | 2.418 |  |  | 1.83 |  |  | 1.522
[5 empty] | % Error |  |  |  | 1.148% |  |  | 0.4584% |  |  | 0.7304% |  |  | 0.6305%
|  | GFR |  |  | Arus Injeksi (A) |  |  |  | 1.275 |  |  | 1.7 |  |  | 2.125 |  |  | 2.55 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  |  | 2.5791 |  |  | 1.5044 |  |  | 1.1355 |  |  | 0.94529
[5 empty] | Hasil Uji (s) |  |  |  | 2.62 |  |  | 1.519 |  |  | 1.151 |  |  | 0.96
[5 empty] | % Error |  |  |  | 1.585% |  |  | 0.9736% |  |  | 1.369% |  |  | 1.556%
|  | Kalkulasi Error Terbesar | [6 empty] | 1.585% |  |  | 0.9736% |  |  | 1.369% |  |  | 1.556%
|  | Hasil Asesmen | [6 empty] | 9 |  |  | 9 |  |  | 9 |  |  | 9
|  | Assessment Pengujian Karakteristik Waktu Kerja | [10 empty] | 9
3.3 |  | Pengujian Arus Kerja OCR Moment/Highset LV
|  | NO | Item Pengujian |  |  | Setting Arus (Ampere) |  |  |  | Hasil Uji Pickup Arus (Ampere) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 |  |  | 17.3 |  |  |  | 17.415 |  | 0.6647% |  | 9 |  | -1 | PHHPTOC1 OPERATE
|  | 2 | OCR HS2 |  |  | 26 |  |  |  | 26.173 |  | 0.6654% |  | 9 |  | -1 | PHHPTOC2 OPERATE
|  | 3 | GFR HS1 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 4 | GFR HS2 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | Assessment Pengujian Arus Kerja OCR Moment | [10 empty] | 9
3.4 |  | Pengujian Waktu Kerja OCR Moment/Highset LV
|  | NO | Item Pengujian |  |  | Setting Waktu Kerja (s) |  |  |  | Hasil Uji Waktu Kerja (s) |  | Nilai Error (Persen) |  | Assessment |  |  | Indikasi
|  | 1 | OCR HS1 |  |  | 0.5 |  |  |  | 0.52 |  | 2% |  | 9 |  | -1 | PHHPTOC1 OPERATE
|  | 2 | OCR HS2 |  |  | 0.3 |  |  |  | 0.318 |  | 1.8% |  | 9 |  | -1 | PHHPTOC2 OPERATE
|  | 3 | GFR HS1 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | 4 | GFR HS2 | [8 empty] | 0% |  | 9 |  | #DIV/0!
|  | Assessment Pengujian Waktu Kerja OCR Moment/Highset LV | [10 empty] | 9
3.5 |  | Evaluasi dan Keterangan
3.6 |  | Kesimpulan :
|  | Assessment Pengujian Individu OCR/GFR LV | [10 empty] | 6
Pelaksana | [11 empty] | Supervisi
1 | Riki H
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [11 empty] | ERVAN JAGI M W

## SBEF
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT | : | BEKASI
|  | ULTG | : | BEKASI
4 |  | Setting SBEF
|  | Setting Arus Pickup SBEF |  |  |  | : | 0.95 |  | A
|  | Setting TMS SBEF |  |  |  | : | 0.17
4.1 |  | Pengujian Arus Pickup dan Dropoff SBEF
|  | Jenis Pengujian |  |  | Parameter |  |  | SBEF
|  | Pickup |  |  | Hasil Uji (A) |  |  | 0.96
[5 empty] | % Error |  |  | 1.053% | [5 empty] | 0
[5 empty] | Assessment |  |  | 9 | [5 empty] | 0
|  | Dropoff |  |  | Hasil Uji (A) |  |  | 0.874
[5 empty] | % Rasio DO/PU |  |  | 91.04% | [5 empty] | 1
[5 empty] | Assessment |  |  | 6 | [5 empty] | 0
|  | Assessment Pengujian Pickup dan Dropoff | [7 empty] | 6
4.2 |  | Pengujian Karakteristik Waktu Kerja SBEF
|  | Poin Pengujian |  |  | Parameter |  |  | 1.5 x Iset |  |  | 2.0 x Iset | 2.5 x Iset | 3.0 x Iset
|  | SBEF |  |  | Arus Injeksi (A) |  |  | 1.425 |  |  | 1.9 | 2.375 | 2.85 | 0
[5 empty] | Hasil Kalkulasi (s) |  |  | 40.8 |  |  | 20.4 | 13.6 | 10.2
[5 empty] | Hasil Uji (s) |  |  | 41.13 |  |  | 20.468 | 13.636 | 10.224
[5 empty] | % Error |  |  | 0.8088% |  |  | 0.3333% | 0.2647% | 0.2353%
|  | Kalkulasi Error Terbesar | [5 empty] | 0.8088% |  |  | 0.3333% | 0.2647% | 0.2353%
|  | Hasil Asesmen | [5 empty] | 9 |  |  | 9 | 9 | 9
|  | Assessment Pengujian Karakteristik Waktu Kerja | [7 empty] | 9
4.3 |  | Evaluasi dan Keterangan
4.4 |  | Kesimpulan :
|  | Assessment Pengujian Individu SBEF | [7 empty] | 6
Pelaksana | [10 empty] | Supervisi
1 | Riki H.
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [10 empty] | ERVAN JAGI M W

## UJI FUNGSI
PT PLN (Persero) Transmisi Jawa Bagian Tengah
|  | UPT |  | : | BEKASI
|  | ULTG |  | : | BEKASI
5.1 |  | Pengujian Fungsi Main Proteksi
|  | Fungsi Proteksi |  |  |  | Pengujian Fasa | Kinerja Acuan |  |  |  | Hasil Uji *) | Assessment | Indikasi Relai, Annunciator & Lockout
|  | DIFF |  |  |  | RST HV | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | Diff Trip, 87T Diff Trip, LO F86.1
|  | DIFF |  |  |  | RST LV | Trip 3 fasa, Lockout, PMT HV dan LV Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  | OK | 9 | Diff Trip, 87T Diff Trip, LO F86.1
|  | REF HV |  |  |  | HV | Trip 3 fasa, Lockout, PMT HV dan LV Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  | OK | 9 | HV REF Trip, REF HV, LO F86.1
|  | REF LV |  |  |  | LV | Trip 3 fasa, Lockout, PMT HV dan LV Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  | OK | 9 | LV REF Trip, REF LV, LO F86.1
|  | *) | Jika hasil uji sesuai, input hanya tulisan OK, jika tidak sesuai maka tulis sesuai hasil pengujian
|  | Assessment Pengujian Fungsi Main Proteksi | [7 empty] | 9
5.2 |  | Pengujian Fungsi Backup Proteksi
|  | Fungsi Proteksi |  |  |  | Pengujian Fasa | Kinerja Acuan |  |  |  | Hasil Uji *) | Assessment | Indikasi Relai, Annunciator & Lockout
|  | OCR HV |  |  |  | RST | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | Overcurrent, BPU HV OC/EF Trip, LO -F86.2
|  | OCR HV Moment |  |  |  | RST | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | Overcurrent, BPU HV OC/EF Trip, LO -F86.2
|  | GFR HV |  |  |  | N | Trip 3 fasa, Lockout, PMT HV dan LV Trip |  |  |  | OK | 9 | Earth-fault, BPU HV OC/EF Trip, LO -F86.2
|  | OCR LV |  |  |  | RST | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | Overcurrent, PHLPTOC1 OPERATE
|  | OCR LV HS1 |  |  |  | RST | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | Overcurrent, PHHPTOC1 OPERATE
|  | OCR LV HS2 |  |  |  | RST | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | Overcurrent, PHHPTOC2 OPERATE
|  | GFR LV |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | Earth-fault, EFLPTOC1 OPERATE
|  | GFR LV HS1 |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | GFR LV HS2 |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  |  | 9
|  | SBEF |  |  |  | N | Trip 3 fasa, Lockout, PMT LV Trip |  |  |  | OK | 9 | SBEF, EFLPTOC2 OPERATE, SBEF Trip
|  | *) | Jika hasil uji sesuai, input hanya tulisan OK, jika tidak sesuai maka tulis sesuai hasil pengujian
|  | Assessment Pengujian Fungsi Backup Proteksi | [7 empty] | 9
5.3 |  | Evaluasi dan Keterangan
PENGUJIAN FUNGSI DENGAN PMT DIBATASI, KARENA MEMPERHATIKAN KONDISI PMT. BEBERAPA POIN PENGUJIAN HANYA SAMPAI LOCKOUT BEKERJA
5.4 |  | Kesimpulan :
|  | Assessment Pengujian Fungsi | [7 empty] | 9
Pelaksana | [8 empty] | Supervisi
1 | Riki H.
2 | Rizky W. H.
3 | Edwar D. V.
4
5 | [8 empty] | ERVAN JAGI M W

## DATA VALIDASI (hidden)
LCD Op | SPAR | Trip 1 Fasa R & Reclose | Trip | Trip 3 fasa, Lockout, PMT HV dan LV Trip
Zone 1 Op | STPAR | Trip 1 Fasa S & Reclose | No Trip
Zone 2 Op |  | Trip 1 Fasa T & Reclose
Zone 3 Op |  | Trip 3 Fasa
Trip 3 Fasa & Reclose
Trip & Reclose CB AB CB Busbar Open
Trip & Reclose CB Busbar CB AB Open
Trip & Reclose CB Busbar & AB
Trip 1 Fasa R & Disusul Trip Fasa ST
Trip 1 Fasa S & Disusul Trip Fasa RT
Tidak Trip